## Small_(1.25 - 2")_FCIS_P-Sched.
Location / Tag | Make / Model | Specification Description | Material | Size (in) | MWWP (PSI) | Installation |  | Accessories / Trim
WS-1 | Wilkins SXL | The “Y” type strainer shall be a manufactured import certified to NSF/ANSI/CAN 61. The main body and cover shall be low lead cast bronze (ASTM B 806), the strainer screen shall be 20 mesh 300 series stainless steel and accessible for maintenance without removing the device from the line. The “Y” type strainer shall be a ZURN WILKINS Model SXL. | Main valve body: Cast Bronze ASTM B 806 Access cover & plug: Cast Bronze ASTM B 806 Screens: 20 Mesh Stainless Steel, 300 Series O-ring: Buna Nitrile | 1-1/4" - 2" | 300 psi @ 180°F WOG | Local codes shall govern installation requirements. Unless otherwise specified, the assembly shall be mounted with sufficient clearance for maintenance in accordance with the manufacturers’ instructions and the latest edition of the Uniform Plumbing Code. The installation shall be made so that no part of the unit can be submerged. Horizontal installation with the strainer cap facing downward is the preferred installation orientation; however the strainer will provide protection in any orientation. |  | Blow Down Valve: Wilkins Model 850XL (Ball Valve)
Strainer (Recommended / Optional, Not shown)
Location / Tag | Make / Model | Specification Description | Material | Valve Size (in) | Max. Rated Pressure | Installation | Accessories / Trim
FCIS-1 (Flood Control System) | Wilkins FCIS | The Connected Flood Control System (Model FCIS) shall consist of a Reduced Pressure Principle Assembly (RPP) Model 375ASTW1, a Pilot Operated Solenoid Control Valve (SCV) (Model ZW206), and a Zurn Relief Valve Monitor. The Endpoint Control Box (ECB) shall have an input voltage of 120 VAC, and shall be provided with 24 VDC output. The Endpoint Control Box shall be housed in a water-tight NEMA enclosure, with BACnet communication protocol capability via Ethernet (Cat-5) cable or BMS communication via alarm terminal outputs. Shall provide multiple outputs that are configurable to Normally Open or Normally Closed. The three components of the Zurn Wilkins FCIS, the RP, SVC, and Endpoint Control Box, when combined together shall automatically shut off the water supply in the event of catastrophic relief valve discharge. | Refer to component (375AST, ZW206) specs below. | 1-1/4" - 2" | 175 PSI | Refer to component instalaltion below. | OSY' - Outside Stem & Yoke 'B' - Buttefly Valves (Flange x Flange) BG' - Buttefly Valves (Groove x Groove) BFG' - Buttefly Valves (Flange x Groove) 'BGF' - Buttefly Valves (Groove x Flange)
Flood Control Integrated System
Location / Tag | Make / Model | Specification Description | Material | Valve Size (in) | Max. Rated Pressure | Installation | Accessories / Trim
SCV-1 (Solenoid Control Valve) | Wilkins ZW206 | The Solenoid Control Valve shall be a single seated, line-pressure-operated, diaphragm-actuated, pilot-controlled globe or angle valve. The valve shall seal by means of a corrosion resistant seat and resilient, rectangular seat disc. These and other parts shall be replaceable in the field; all such service and adjustments to be possible without removing the valve from the line. The stem of the basic valve shall be guided top and bottom by integral bushings. The basic valve and its pilot control system shall contain no packing glands or stuffing boxes. The diaphragm shall not be used as a seating surface, nor shall pistons be used as an operating medium. All internal and external ferrous surfaces shall be coated with a high-quality, FDA Approved blue fusion epoxy coating. The valve shall be certified to NSF/ANSI/CAN Standard 61. The Solenoid Control Valve shall be a ZURN WILKINS Model ZW206. | Main Valve Body: Ductile Iron ASTM A536 Main Valve Bonnet: Ductile Iron ASTM A536 Disc Guide: Stainless Steel Seat: Stainless Steel Disc: Buna-N Rubber Diaphragm: Nylon Reinforced Buna-N Stem & Spring: Stainless Steel Coating: FDA Approved Fusion Epoxy | 1-1/4" - 2" | Threaded: 400 PSI | Local codes shall govern installation requirements. Unless otherwise specified, the assembly shall be mounted at a minimum of 12" (305mm) and a maximum of 30" (762mm) above adequate drains with sufficient side clearance for testing and maintenance. The installation shall be made so that no part of the unit can be submerged. | 'Z' - Position Indicator 'C' - Hydraulic Check 'L' - Closing Speed Control 'O' - Opening Speed Control 'F' - Atmospheric Drain
Solenoid Operated Automatic Control Valve
Location / Tag | Make / Model | Specification Description | Material | Size (in) | MWWP (PSI) | Installation | Accessories / Trim
BFP-1 | Wilkins' Model 975XL3 | Wilkins' Model 975XL3 ASSE® 1013 Listed Reduced Pressure Principle Backflow Preventer (certified to NSF/ANSI/CAN 61) is rated for 180°F, 175 PSI, comes standard with low lead bronze (ASTM B 584) full port ball valves, main body and access covers. The seat ring and all internal polymers shall be Noryl™. The seat disc elastomers shall be silicone. Test cocks shall be accessible from the top of the assembly. | Main valve body: Low Lead Cast Bronze ASTM B 584 Access covers: Low Lead Cast Bronze ASTM B 584 Fasteners: Stainless Steel, 300 Series Elastomers: Silicone (FDA Approved) Buna Nitrile (FDA Approved) Polymers: Noryl™ Springs: Stainless Steel, 300 Series Ball valve handles: Stainless Steel | 1-1/4" - 2" | 300 psi @ 180°F WOG | Installation of Backflow Preventers must be performed by qualified, licensed personnel. The installer should be sure the proper device has been selected for the particular installation. Faulty installation could result in an improperly functioning device. Comply with authorities having jurisdiction. | Wye Strainer / Air Gap / Test Kit
Backflow Prevention Assembly
Location / Tag | Make / Model | Specification Description | Material | Size (in) | Outlet Pipe Size (Type) | Installation
AG-X | Wilkins AG-4 | Air-Gap Fitting: ASME A112.1.2, matching backflow-preventer connection. | Body: Cast grey iron, epoxy painted Bolts: Steel, zinc plated | 1-1/4"-1-1/2" | 1" NPT | Local codes shall govern installation requirements. To be installed in accordance with the manufacturers' instructions and the latest edition of the Uniform Plumbing Code.
AG-Y | Wilkins AG-5 | Air-Gap Fitting: ASME A112.1.2, matching backflow-preventer connection. | Body: Cast grey iron, epoxy painted Bolts: Steel, zinc plated | 2" | 2" NPT | Local codes shall govern installation requirements. To be installed in accordance with the manufacturers' instructions and the latest edition of the Uniform Plumbing Code.
Air Gap

## Large_(2.5"-10")_FCIS_P-Sched.
Location / Tag | Make / Model | Specification Description | Material | Size (in) | MWWP (PSI) | Installation |  | Accessories / Trim
WS-1 | Wilkins FSC | The Ductile Iron “Y” type strainer shall meet the requirements of NSF/ANSI/CAN 372, and MIL-S-16293F Type 2. The main body and access cover shall be ductile iron ASTM A536 with an NSF/ANSI/CAN 61 certified Fusion Epoxy Finish coating inside and out. The integral strainer screen shall be accessible for cleaning without removing the device from the line. The Ductile Iron “Y” type strainer shall be a ZURN WILKINS Model FSC. | Main valve body: Ductile Iron ASTM A536 Access cover & plug: Ductile Iron ASTM A536 Screens: Perforated Stainless Steel, 300 Series O-ring: Buna Nitrile Coating: Fusion Epoxy Finish (Meets requirements of NSF/ANSI/CAN 61) | 2-1/2" - 10" | 200 psi @ 150°F WOG | Local codes shall govern installation requirements. Unless otherwise specified, the assembly shall be mounted with sufficient clearance for maintenance in accordance with the manufacturers’ instructions and the latest edition of the Uniform Plumbing Code. The installation shall be made so that no part of the unit can be submerged. Horizontal installation with the strainer cap facing downward is the preferred installation orientation; however the strainer will provide protection in any orientation. |  | Blow Down Valve: Wilkins Model 850XL (Ball Valve)
Strainer
Location / Tag | Make / Model | Specification Description | Material | Valve Size (in) | Max. Rated Pressure | Installation | Accessories / Trim
FCIS-1 (Flood Control System) | Wilkins' Model FCIS | The Connected Flood Control System (Model FCIS) shall consist of a Reduced Pressure Principle Assembly (RPP) Model 375ASTW1, a Pilot Operated Solenoid Control Valve (SCV) (Model ZW206), and a Zurn Relief Valve Monitor. The Endpoint Control Box (ECB) shall have an input voltage of 120 VAC, and shall be provided with 24 VDC output. The Endpoint Control Box shall be housed in a water-tight NEMA enclosure, with BACnet communication protocol capability via Ethernet (Cat-5) cable or BMS communication via alarm terminal outputs. Shall provide multiple outputs that are configurable to Normally Open or Normally Closed. The three components of the Zurn Wilkins FCIS, the RP, SVC, and Endpoint Control Box, when combined together shall automatically shut off the water supply in the event of catastrophic relief valve discharge. | Refer to component (375AST, ZW206) specs below. | 2-1/2" - 10" | 175 PSI | Refer to component instalaltion below. | OSY' - Outside Stem & Yoke 'B' - Buttefly Valves (Flange x Flange) BG' - Buttefly Valves (Groove x Groove) BFG' - Buttefly Valves (Flange x Groove) 'BGF' - Buttefly Valves (Groove x Flange)
Flood Control Integrated System
Location / Tag | Make / Model | Specification Description | Material | Valve Size (in) | Max. Rated Pressure | Installation | Accessories / Trim
SCV-1 (Solenoid Control Valve) | Wilkins' Model ZW206 | The Solenoid Control Valve shall be a single seated, line-pressure-operated, diaphragm-actuated, pilot-controlled globe or angle valve. The valve shall seal by means of a corrosion resistant seat and resilient, rectangular seat disc. These and other parts shall be replaceable in the field; all such service and adjustments to be possible without removing the valve from the line. The stem of the basic valve shall be guided top and bottom by integral bushings. The basic valve and its pilot control system shall contain no packing glands or stuffing boxes. The diaphragm shall not be used as a seating surface, nor shall pistons be used as an operating medium. All internal and external ferrous surfaces shall be coated with a high-quality, FDA Approved blue fusion epoxy coating. The valve shall be certified to NSF/ANSI/CAN Standard 61. The Solenoid Control Valve shall be a ZURN WILKINS Model ZW206. | Main Valve Body: Ductile Iron ASTM A536 Main Valve Bonnet: Ductile Iron ASTM A536 Disc Guide: Stainless Steel Seat: Stainless Steel Disc: Buna-N Rubber Diaphragm: Nylon Reinforced Buna-N Stem & Spring: Stainless Steel Coating: FDA Approved Fusion Epoxy | 2-1/2" - 10" | Flanged: ANSI Class 150 - 250 PSI ANSI Class 300 - 400 PSI Threaded: 400 PSI Grooved: 300 PSI | Local codes shall govern installation requirements. Unless otherwise specified, the assembly shall be mounted at a minimum of 12" (305mm) and a maximum of 30" (762mm) above adequate drains with sufficient side clearance for testing and maintenance. The installation shall be made so that no part of the unit can be submerged. | 'Z' - Position Indicator 'C' - Hydraulic Check 'L' - Closing Speed Control 'O' - Opening Speed Control 'F' - Atmospheric Drain
Solenoid Operated Automatic Control Valve
Location / Tag | Make / Model | Specification Description | Material | Valve Size (in) | Rated Pressure | Installation | Accessories / Trim
BFP-1 | Wilkins' Model 375AST | The Reduced Pressure Principle Backflow Prevention Assembly shall be certified to NSF/ANSI/CAN 61 and 372, ASSE® Listed 1013, and supplied with full port gate valves. The main body and access cover shall b 304L Stainless Steel, the seat ring and check valve shall be NORYL™, the stem shall be stainless steel (ASTM A 276) and the seat disc elastomers shall be EPDM. The checks and the relief valve shall be accessible for maintenance without removing the device from the line. The Reduced Pressure Principle Backflow Prevention Assembly shall be a ZURN WILKINS Model 375AST | Main Valve Body: 304L Stainless steel Access covers: 304L Stainless steel Coatings: FDA Approved electrostatic epoxy finish Internals: Stainless steel, 300 Series NORYL™ Fasteners & Springs: Stainless Steel, 300 Series Seal rings: EPDM (FDA approved) O-rings: Buna Nitrile (FDA approved) Sensing line: Stainless Steel, braided hose | 2-1/2" - 10" | 175 PSI | Local codes shall govern installation requirements. Unless otherwise specified, the assembly shall be mounted at a minimum of 12" (305mm) and a maximum of 30" (762mm) above adequate drains with sufficient side clearance for testing and maintenance. The installation shall be made so that no part of the unit can be submerged. | Wye Strainer / Air Gap / Test Kit
Backflow Prevention Assembly
Location / Tag | Make / Model | Specification Description | Material | Size (in) | Outlet Pipe Size (Type) | Installation
AG-X | Wilkins AG-6 | Air-Gap Fitting: ASME A112.1.2, matching backflow-preventer connection. | Body: Cast grey iron, epoxy painted Bolts: Steel, zinc plated | 2-1/2" - 6" | 3" NPT | Local codes shall govern installation requirements. To be installed in accordance with the manufacturers' instructions and the latest edition of the Uniform Plumbing Code.
AG-Y | Wilkins AG-7 | Air-Gap Fitting: ASME A112.1.2, matching backflow-preventer connection. | Body: Cast grey iron, epoxy painted Bolts: Steel, zinc plated | 8"-10" | 4" NPT | Local codes shall govern installation requirements. To be installed in accordance with the manufacturers' instructions and the latest edition of the Uniform Plumbing Code.
Air Gap