## Single_PRV_(500XL3)
Location / Tag | Make / Model | Specification Description | Material | Size (in) | MWWP (PSI) | Inlet Pressure (PSI)
SOV-1 | Wilkins 850XL | Shall be full port, all-brass or bronze construction with replaceable Teflon seat ring, two-piece union or three-piece bolted design as scheduled herein. | Body: Low lead Bronze ASTM B 584 Ball: Chrome plated low lead brass Seat: TFE virgin teflon | 3/8" - 2" | 175 PSI | 135
SOV-1 | Wilkins Model 49 | Resilient-seated and high-performance butterfly valves shall be full lug type suitable for bidirectional dead-end service at rated pressure without use of downstream flange. Conforming to ANSI Class 150 or Class flange drilling as scheduled herein. | Main body: Ductile Iron ASTM A 536 Handwheel: Cast Iron ASTM A 48 Disc: Ductile Iron ASTM A 536 with EPDM encapsulation Stem Bearings: Bronze ASTM B 584 Coating: AWWA C550 Compliant fusion- bond epoxy finish (meets the re- quirements of NSF/ANSI/CAN 61) | 2-1/2" - 3" | 175 PSI | 135
Shut-off Valve Schedule
Location / Tag | Make / Model | Specification Description | Material | Size (in) | MWWP (PSI) | Inlet Pressure (PSI) | Rated Flow (GPM) | Installation |  |  |  | Accessories / Trim
WS-1 | Wilkins SXL | The “Y” type strainer shall be a manufactured import certified to NSF/ANSI/CAN 61. The main body and cover shall be low lead cast bronze (ASTM B 806), the strainer screen shall be 20 mesh 300 series stainless steel and accessible for maintenance without removing the device from the line. The “Y” type strainer shall be a ZURN WILKINS Model SXL. | Main valve body: Cast Bronze ASTM B 806 Access cover & plug: Cast Bronze ASTM B 806 Screens: 20 Mesh Stainless Steel, 300 Series O-ring: Buna Nitrile | 3/8" - 3" | 300 psi @ 180°F WOG | 135 | 0-500 | Install wye pattern strainers for water on supply side of each [control valve] [water pressure-reducing valve] [solenoid valve] [and] [pump]. Local codes shall govern installation requirements. Unless otherwise specified, the assembly shall be mounted in accordance with the latest edition of the Uniform Plumbing Code. If installed below grade, be certain adequate drainage is provided to prevent the device from being submerged. Horizontal installation with the strainer cap facing downward is the preferred installation orientation; however the strainer will provide protection in any orientation. |  |  |  | Blow Down Valve: Wilkins Model 850XL (Ballv Valve)
Strainer Schedule
Location / Tag | Make / Model | Specification Desctiption | Material | Size (in) | MWWP (PSI) | Inlet Pressure (PSI) | Outlet Pressure (PSI) | Pressure Reduction Ratio | Design Flow Rate (Min/Max) | Allowable Fall-Off | Installation |  | Accessories / Trim
PRV-1 | Wilkins Model 500XL3 | The Pressure Reducing Valve shall be certified to NSF/ANSI/CAN 61 & 372, consisting of a low lead silicon bronze body and silicon bronze bell housing, and a bolt to adjust the downstream pressure. The bronze bell housing shall be threaded to the body. The assembly shall be of the balanced piston design and shall reduce pressure in both flow and and no-flow conditions with restricting tailpieces for ideal fall-off and low-flow bypass performance. The assembly shall be accessible for maintenance without having to remove the body from the line. Shall include a removable cartridge and corrosion resistant materials. The Pressure Reducing Valve shall be a ZURN WILKINS Model 500XL3DUBP. | Main valve body: Low lead cast bronze ASTM B806 Bell housing: Cast bronze ASTM B806 Fasteners: Stainless steel, 300 Series Stem: Stainless steel, 300 Series Plunger: Stainless steel, 300 series Elastomers: Buna Nitrile (FDA approved), EPDM (FDA approved) Springs: Stainless steel, 300 series Cartridge: Noryl™ | 1" - 3" | 400 PSI | 135 | 75 | 1.8 | 0 - 80 GPM | <10 PSI | Local codes shall govern installation requirements. Unless otherwise specified, the assembly shall be installed in accordance with the manufacturers’ instructions and the latest edition of the Uniform plumbing Code. The assembly shall be installed with sufficient side clearance for testing and maintenance. The Model 500XL3F may be installed in any position. Multiple installations, in series (back to back) are recommended for wide demand variations or where the desired pressure reduction is more than 3 to 1 (ie: 150 psi inlet reduced to 50 psi outlet). CAUTION: Anytime a reducing valve is adjusted, a pressure gauge must be used downstream to verify correct pressure setting. Do not bottom adjustment bolt on bell housing. |  | Blow Down Valve: Wilkins Model 850XL (Ballv Valve)
Pressure Reducing Valve Schedule

## PRV_(500XL3)w-Low_Flow_BP
Location / Tag | Make / Model | Specification Description | Material | Size (in) | MWWP (PSI) | Inlet Pressure (PSI)
SOV-1 | Wilkins Model 49 | Resilient-seated and high-performance butterfly valves shall be full lug type suitable for bidirectional dead-end service at rated pressure without use of downstream flange. Conforming to ANSI Class 150 or Class flange drilling as scheduled herein. | Main body: Ductile Iron ASTM A 536 Handwheel: Cast Iron ASTM A 48 Disc: Ductile Iron ASTM A 536 with EPDM encapsulation Stem Bearings: Bronze ASTM B 584 Coating: AWWA C550 Compliant fusion- bond epoxy finish (meets the re- quirements of NSF/ANSI/CAN 61) | 2-1/2" - 10" | 175 PSI | 135
Shut-off Valve Schedule
Location / Tag | Make / Model | Specification Description | Material | Size (in) | MWWP (PSI) | Inlet Pressure (PSI) | Rated Flow (GPM) | Installation |  |  |  | Accessories / Trim
WS-1 | Wilkins Model FSC | The Ductile Iron “Y” type strainer shall meet the requirements of NSF/ANSI 372, and MIL-S-16293F Type 2. The main body and access cover shall be ductile iron ASTM A536 with an NSF/ANSI/CAN 61 certified Fusion Epoxy Finish coating inside and out. The integral strainer screen shall be accessible for cleaning without removing the device from the line. | Main valve body: Ductile Iron ASTM A536 Access cover: Ductile Iron ASTM A536 Coatings: Fusion Epoxy Finish (Meets requirements of NSF/ANSI/CAN 61) Screens: Perforated Stainless Steel, 300 Series | 2-1/2" - 12" | 200 psi @ 150°F WOG | 135 | 0-4500 | Local codes shall govern installation requirements. Unless otherwise specified, the assembly shall be mounted with sufficient clearance for maintenance in accordance with the manufacturers’ instructions and the latest edition of the Uniform Plumbing Code. The installation shall be made so that no part of the unit can be submerged. Horizontal installation with the strainer cap facing downward is the preferred installation orientation; however the strainer will provide protection in any orientation. |  |  |  | Blow Down Valve: Wilkins Model 850XL (Ballv Valve)
Strainer Schedule
Location / Tag | Make / Model | Specification Desctiption | Material | Size (in) | MWWP (PSI) | Inlet Pressure (PSI) | Outlet Pressure (PSI) | Pressure Reduction Ratio | Design Flow Rate (Min/Max) | Allowable Fall-Off | Installation
PRV-1 | Wilkins Model 500XL3F | The Pressure Reducing Valve shall be certified to NSF/ANSI/CAN 61 & 372, consisting of a low lead silicon bronze body and silicon bronze bell housing, and a bolt to adjust the downstream pressure. The bronze bell housing shall be affixed to the body with stainless steel bolts. The assembly shall be of the balanced piston design and shall reduce pressure in both flow and noflow conditions with integral venturi for improved flow performance. The assembly shall be accessible for maintenance without having to remove the body from the line. Shall include a removable cartridge and corrosion resistant materials. The Pressure Reducing Valve shall be tapped and plugged to accept a Model 1-500XL3BPK low flow by-pass kit. The Pressure Reducing Valve shall be a ZURN WILKINS Model 500XL3F. | Main valve body: Low lead cast bronze ASTM B806 Bell housing: Cast bronze ASTM B806 Fasteners: Stainless steel, 300 Series Stem: Stainless steel, 300 Series Plunger: Low lead cast bronze ASTM B806 Elastomers: Buna Nitrile (FDA approved), EPDM (FDA approved) Springs: Chrome Silicon, Epoxy Coated Cartridge: Noryl™ | 3" | 400 PSI | 135 | 75 | 1.8 | 20-250 GPM | <10 PSI | Local codes shall govern installation requirements. Unless otherwise specified, the assembly shall be installed in accordance with the manufacturers’ instructions and the latest edition of the Uniform plumbing Code. The assembly shall be installed with sufficient side clearance for testing and maintenance. The Model 500XL3F may be installed in any position. Multiple installations, in series (back to back) are recommended for wide demand variations or where the desired pressure reduction is more than 3 to 1 (ie: 150 psi inlet reduced to 50 psi outlet). CAUTION: Anytime a reducing valve is adjusted, a pressure gauge must be used downstream to verify correct pressure setting. Do not bottom adjustment bolt on bell housing.
PRV-1-BP | Wilkins Model 500XL3BPK (Bypass Kit) | The Pressure Reducing Valve shall be certified to NSF/ANSI/CAN 61 & 372, consisting of a low lead silicon bronze body and silicon bronze bell housing, and a bolt to adjust the downstream pressure. The bronze bell housing shall be threaded to the body. The assembly shall be of the balanced piston design and shall reduce pressure in both flow and and no-flow conditions with restricting tailpieces for ideal fall-off and low-flow bypass performance. The assembly shall be accessible for maintenance without having to remove the body from the line. Shall include a removable cartridge and corrosion resistant materials. The Pressure Reducing Valve shall be a ZURN WILKINS Model 500XL3DUBP. | Main valve body: Low lead cast bronze ASTM B806 Bell housing: Cast bronze ASTM B806 Fasteners: Stainless steel, 300 Series Stem: Stainless steel, 300 Series Plunger: Stainless steel, 300 series Elastomers: Buna Nitrile (FDA approved), EPDM (FDA approved) Springs: Stainless steel, 300 series Cartridge: Noryl™ | 1" | 400 PSI | 135 | 80 | 1.6875 | 0-20 GPM | <10 PSI | Local codes shall govern installation requirements. Unless otherwise specified, the assembly shall be mounted in accordance with the manufacturer's instructions and the latest edition of the Uniform Plumbing Code. The assembly shall be installed with sufficient side clearance for testing and maintenance. The Model 500XL3DUBP may be installed in any position. The Model 500XL3DUBP should be used as a parallel low flow bypass to handle flows according to table below. Set the bypass valve approximately 5 to 10 PSI higher than the large valve in a high-flow / low-flow parallel PRV battery. Multiple installations, in series (back to back) are recommended where the desired pressure reduction is more than 3 to 1 (ie: 150 psi inlet reduced to 50 psi outlet). Caution: Anytime a pressure reducing valve is adjusted, a pressure gauge must be used downstream to verify correct pressure setting. Do not bottom-out adjustment bolt on bell housing.
PRV-2
PRV-2-BP
Pressure Reducing Valve Schedule